Software Requirements Document

for 200 mm Factory Automation Project

Prepared By : Ramkumar M

HiCore Software Technologies Private Limited

Version:  1.0

Table of Contents

1.	Introduction	5

1.1.	Purpose	5

1.2.	Scope	5

2.	Standard and Compliance	5

2.1.	Applicable SEMI Standards	5

2.2.	GEM-200 Compliance Scope	6

2.3.	Mandatory GEM Features	6

3.	System Overview	7

3.1.	Product Perspective	7

3.2.	GEM-200 Functional Overview	7

3.3.	Operating Environment (200 mm Equipment)	8

3.4.	Assumptions and Constraints	8

4.	GEM Functional Requirements	9

4.1.	HSMS Communication	9

4.2.	SECS-II Message Support	11

4.3.	GEM State Models	12

4.4.	Alarm Management	13

4.5.	Event and Report Management	15

4.6.	Variable Data Management (VID / SVID)	15

4.7.	Remote Command Handling	16

4.8.	Recipe Management	17

4.9.	Terminal Services	18

4.10.	Time Management	19

5.	System Architecture Requirements	20

5.1.	Logical Architecture Overview	20

5.2.	GEM-200 Core Components	21

6.	Equipment Adapter Requirements	24

6.1.	Equipment Control Interface	24

6.2.	Equipment Status Interface	24

6.3.	Equipment Alarm Interface	24

6.4.	Equipment Event Interface	25

7.	Configuration Management	25

7.1.	Configuration Storage	25

7.2.	Runtime Configuration Handling	26

7.3.	Version and Change Control	26

8.	Logging and Diagnostics	26

8.1.	HSMS and SECS-II Message Logging	26

8.2.	Alarm and Event History	27

8.3.	Remote Command and Adapter Logging	27

8.4.	Log Retention and Rotation	27

9.	Reliability and Data Integrity	28

9.1.	Spooling Requirements	28

9.2.	Message Recovery and Reconnect Handling	28

9.3.	Data Consistency Guarantees	28

10.	Optional Engineering Features	29

10.1.	Simulation Mode	29

10.2.	Host Simulator	30

10.3.	Equipment Simulator	30

10.4.	Diagnostic / Engineering User Interface	31

11.	Performance Requirements	31

12.	Security Requirements	31

13.	Verification and Test Requirements	32

13.1.	SEMI GEM Mandatory Test Coverage	32

13.2.	Host Integration Testing	32

13.3.	Factory Acceptance Testing (FAT)	33

14.	Supported SECS-II Streams and Functions	34

Version History

| Version | Description | Date |
| --- | --- | --- |
| 1.0 | Initial Draft |  |

# Introduction

## Purpose

The purpose of this Software Requirements Specification (SRS) is to define the high-level functional and operational requirements for a GEM-200 (200 mm) Equipment GEM Controller. The system enables standardized communication between the equipment and factory Host systems in compliance with SEMI E30 (GEM), SEMI E37 (HSMS-SS), and SEMI E5 (SECS-II).

## Scope

This SRS defines the requirements for a GEM-200 Equipment GEM Controller supporting SEMI-compliant HSMS-SS, SECS-II, and GEM behaviour. The scope includes state management, alarms, events, reports, variable data collection, remote commands, recipes, terminal services, configuration, logging, spooling, and time management, with equipment integration managed through a defined Equipment Adapter interface. Mechanical and process-specific equipment design are excluded from scope.

# Standard and Compliance

## Applicable SEMI Standards

    - The GEM-200 Equipment GEM Controller shall comply with the following SEMI standards:

    - SEMI E30 (GEM) shall define standard equipment behaviour, including communication and control state models, alarm management, event and report handling, remote command execution, and recipe management.

    - SEMI E37 (HSMS-SS) shall define the TCP/IP–based communication protocol used between the equipment and factory Host systems.

    - SEMI E5 (SECS-II) shall define the structure and content of SECS-II messages, including streams, functions, message headers, and data items.

    - SEMI E4 (SECS-I Message Structure) shall define common SECS message framing and header conventions applicable to SECS-based communication.

## GEM-200 Compliance Scope

    - This SRS defines the GEM-200 compliance scope for a 200 mm Equipment GEM Controller.

    - The system shall comply with the mandatory requirements of SEMI E30 (GEM) and support Host communication using SEMI E37 (HSMS-SS) and

SEMI E5 (SECS-II).

    - The GEM-200 compliance scope includes:

- HSMS-SS communication in Passive (Equipment) mode

- SECS-II message processing and protocol error handling

- Communication and control state models

- Alarm, event, and report management.

- Variable data collection (VID / SVID)

- Remote command execution

- Recipe management and terminal services

    - Supporting features such as logging, spooling, configuration management, and time management are included to ensure reliable factory operation.

    - Optional engineering features (e.g., simulation, host/equipment simulators, diagnostic UI) may be provided without affecting GEM-200 compliance.

## Mandatory GEM Features

    - The system shall support HSMS-SS communication in Passive (Equipment) mode.

    - The system shall support SECS-II messaging in accordance with SEMI E5.

    - The system shall implement GEM communication and control state models.

    - The system shall support alarm management, event and report handling, and variable data collection (VID / SVID).

    - The system shall support remote command execution and recipe management.

    - The system shall support terminal services and protocol error handling.

# System Overview

## Product Perspective

    - The GEM-200 Equipment GEM Controller is a software subsystem that enables standardized communication between 200 mm semiconductor manufacturing equipment and factory Host systems.

    - The system operates as an interface layer between the equipment control system and the factory automation environment.

    - The GEM Controller shall be designed to be independent of equipment hardware, using a defined Equipment Adapter interface.

    - The solution shall support SEMI GEM standards and integrate into existing factory systems without impacting core equipment control logic.

## GEM-200 Functional Overview

    - The GEM-200 Equipment GEM Controller shall provide standardized Host–Equipment communication for 200 mm semiconductor tools.

    - The system shall support HSMS-SS and SECS-II messaging to exchange status, control, alarm, and process information with the Host.

    - The system shall implement GEM-defined behaviours, including:

  - Communication and control state management

  - Alarm reporting and acknowledgment.

  - Event and data reporting

  - Variable data collection (VID / SVID)

  - Remote command execution

  - Recipe management

    - The system shall ensure SEMI-compliant operation, reliable factory integration, and support for client acceptance and audits.

## Operating Environment (200 mm Equipment)

    - The GEM-200 Equipment GEM Controller shall operate within 200 mm semiconductor manufacturing equipment environments.

    - The system shall interface with factory Host systems over standard TCP/IP networks using HSMS-SS.

    - The system shall run on industrial PC or embedded controller platforms typically used in semiconductor equipment.

    - The GEM Controller shall integrate with existing equipment control systems (e.g., PLCs or tool controllers) through a defined Equipment Adapter interface.

    - The operating environment shall support continuous operation in automated factory conditions.

## Assumptions and Constraints

    - Assumptions

The equipment is 200 mm semiconductor manufacturing equipment intended for factory automation environments. A factory Host system supporting SEMI GEM standards is available for integration, and the network infrastructure supports TCP/IP communication required for HSMS-SS operation. The equipment control systems expose the required data, status, and command interfaces necessary for interaction with the GEM Controller.

    - Constraints

The GEM Controller shall comply with SEMI E30, SEMI E37, SEMI E5, and SEMI E4 standards and shall operate in HSMS Passive (Equipment) mode for production use. The GEM Controller shall not directly control mechanical motion or safety-critical hardware, with all equipment-specific logic isolated within the Equipment Adapter layer. Performance and security requirements shall align with applicable factory IT policies and OEM guidelines.

# GEM Functional Requirements

## HSMS Communication

    - The system shall support HSMS-SS communication in accordance with SEMI E37 for Host–Equipment interaction.

    - The GEM Controller shall operate in Passive (Equipment) mode as the mandatory configuration for production environments.

    - The system may support HSMS Active Mode for engineering, testing, and simulation purposes only, and such support shall not impact production behaviour or GEM-200 compliance.

    - The system shall reliably establish, maintain, and terminate HSMS sessions with the factory Host.

    - The equipment shall listen on a configured TCP/IP port for Host-initiated HSMS connections.

    - The Host shall initiate communication using Select.req, and the system shall complete session establishment using Select.rsp.

    - The system shall allow only one active HSMS session at any given time.

    - When disconnected, the system shall remain in a passive listening state ready for Host reconnection.

    - The system shall support all mandatory HSMS control messages as defined in SEMI E37.

    - Supported HSMS control messages shall include:

| HSMS Control Message | Purpose |
| --- | --- |
| Select.req / Select.rsp | Establishes and confirms an HSMS communication session between the Host and the equipment. |
| Deselect.req / Deselect.rsp | Gracefully terminates an active HSMS communication session. |
| Linktest.req / Linktest.rsp | Verifies that the HSMS connection is active and responsive. |
| Reject.req | Indicates that an invalid, unexpected, or unsupported HSMS message was received. |
| Separate.req | Forces immediate termination of the HSMS session due to errors or abnormal conditions. |

    - HSMS control messages shall be processed according to the current HSMS session state, ensuring correct protocol behaviour and state transitions.

    - The system shall implement and manage HSMS session timers in accordance with SEMI E37, including:

- Reply timeout

- Connection separation timeout

- Control transaction timeout

- Not-selected timeout

    - HSMS timer values shall be configurable, with default values aligned to SEMI recommendations.

    - Expiration of HSMS session timers shall trigger appropriate error handling and session recovery actions.

    - The system shall use an independent message receiver mechanism to continuously monitor the TCP/IP connection.

    - Message reception shall be non-blocking and independent of GEM message processing logic.

    - Received HSMS frames shall be validated and forwarded to the SECS-II processing layer.

    - Communication errors and unexpected disconnects shall be detected and managed gracefully without impacting system stability.

    - The system shall support HSMS byte-level message framing using the standard structure:

Message Length + HSMS Header + SECS-II Message Body.

    - The system shall correctly frame and deframe all incoming and outgoing HSMS messages.

    - The system shall validate message length and HSMS header fields prior to message processing.

    - The system shall correctly manage fragmented or combined TCP packets.

    - Invalid or malformed messages shall be detected, logged, and managed using standard GEM error responses.

## SECS-II Message Support

    - The system shall support SECS-II message structures in accordance with SEMI E5.

    - The system shall correctly process SECS-II primary and secondary messages.

    - The system shall manage SECS-II message header fields, including:

- Stream

- Function

- W-bit (Wait-for-Reply)

- Device ID

- System Bytes

    - The system shall ensure correct correlation between request and response messages using System Bytes.

    - The system shall support SECS-II data item types as defined in SEMI E5, including:

- List (L)

- ASCII (A)

- Binary (B)

- Unsigned Integers (U1, U2, U4)

- Signed Integers (I1, I2, I4)

- Boolean

    - The system shall correctly encode and decode SECS-II data items exchanged with the Host.

    - SECS-II data items shall be validated for data type, length, and structure before processing.

    - The system shall detect SECS-II protocol and formatting errors in accordance with SEMI E5.

    - The system shall generate appropriate S9Fx error messages for:

- Invalid stream or function values

- Incorrect message structure

- Invalid data item format

- Unsupported or unexpected messages

    - Protocol error responses shall be sent within required SECS-II timing limits.

    - All SECS-II protocol errors shall be logged for diagnostics, troubleshooting, and audit purposes.

## GEM State Models

    - The system shall implement the GEM Communication State Model in accordance with SEMI E30.

    - Supported communication states shall include:

- OFFLINE

- ONLINE LOCAL

- ONLINE REMOTE

    - The system shall always maintain the current communication state internally.

    - Communication state transitions shall occur based on Host commands and equipment internal conditions.

    - Communication state changes shall be reported to the Host when required by GEM.

    - The system shall implement the GEM Control State Model in accordance with SEMI E30.

    - Supported control states shall include:

- LOCAL

- REMOTE

    - The system shall restrict remote command execution to the REMOTE control state.

    - Control state transitions shall be initiated by the Host or operator, subject to GEM rules and equipment conditions.

    - Control state changes shall be reported to the Host as required by GEM.

## Alarm Management

    - The system shall implement GEM-compliant alarm management in accordance with SEMI E30.

    - The system shall maintain a defined alarm list, including:

- Alarm Identifier (ALID)

- Alarm description

- Alarm severity or type

    - The system shall support the following alarm types:

- Equipment alarms

- Process alarms

- Warning and information alarms

    - Alarm definitions shall be configurable and mapped to equipment-level alarms via the Equipment Adapter.

    - Each alarm shall have a clearly defined set and clear behaviour.

    - The system shall report alarm set and clear events using SECS-II Stream 5 messages.

    - The system shall generate S5F1 (Alarm Report Send) when an alarm is set or cleared.

    - The system shall process S5F2 (Alarm Report Acknowledge) responses from the Host.

    - Alarm reports shall include the required alarm identifier and alarm state information.

    - Alarm reporting shall comply with GEM timing and sequencing requirements.

    - The system shall support alarm query requests using SECS-II Stream 5.

    - The system shall support the following alarm query functions:

- S5F5 – List all defined alarms.

- S5F7 – List all active alarms.

    - The system shall return accurate and up-to-date alarm information to the Host.

    - Alarm query responses shall comply with SEMI E30 and SECS-II formatting rules.

## Event and Report Management

    - The system shall implement the GEM event and report model in accordance with SEMI E30.

    - The system shall support Collection Event IDs (CEIDs) to represent equipment events and GEM-related events.

    - Each CEID shall be associated with one or more Report IDs (RPTIDs).

    - Each RPTID shall reference one or more Variable IDs (VIDs).

    - CEID, RPTID, and VID definitions shall be configurable and maintainable within the system.

    - The event and report model shall ensure consistent and accurate data reporting to the Host.

    - The system shall support dynamic event–report linking in accordance with SEMI E30.

    - The Host shall be able to define, modify, link, and unlink reports at runtime using standard GEM mechanisms.

    - Changes to report definitions or event–report links shall take effect without requiring a system restart.

    - Dynamic report linking shall not impact system stability or GEM compliance.

    - The system shall report GEM events using S6F11 (Event Report Send) messages.

    - Event reports shall be generated when configured CEIDs are triggered.

    - Each event report may include one or more associated reports (RPTIDs).

    - Event reports shall include the current values of associated VIDs.

    - Event reporting shall comply with GEM timing, sequencing, and SECS-II formatting rules.

## Variable Data Management (VID / SVID)

    - The system shall maintain a defined list of Variable IDs (VIDs) and Status Variable IDs (SVIDs) in accordance with SEMI E30.

    - Each VID and SVID shall have a unique identifier, name, data type, and description.

    - VIDs shall represent measurable equipment or process-related data.

    - SVIDs shall represent equipment status and GEM state information.

    - VID and SVID definitions shall be configurable to meet customer-specific and equipment-specific requirements.

    - The system shall acquire real-time variable values from the equipment through the Equipment Adapter interface.

    - Variable data shall be updated to reflect the current equipment and process state.

    - The system shall ensure accuracy and consistency when reporting VID and SVID values to the Host.

    - Variable data shall be available for Host variable requests, event reports, and data collection functions.

    - Variable data acquisition shall not adversely impact equipment performance or system stability.

    - The system shall support trace and periodic data collection using configured VIDs and SVIDs.

    - Data collection intervals, durations, and triggering conditions shall be configurable.

    - Collected data shall be reported to the Host using standard GEM mechanisms.

    - Trace and periodic data collection shall comply with GEM timing and sequencing requirements.

    - Data collection shall operate reliably without impacting normal equipment operation.

## Remote Command Handling

    - The system shall support GEM remote command execution using S2F41 (Remote Command Send) and S2F42 (Remote Command Acknowledge).

    - Remote commands shall be accepted only when the equipment is in the REMOTE control state.

    - Each remote command shall be identified by a defined command name and associated command parameters.

    - The system shall return remote command execution results to the Host using S2F42.

    - Remote command handling shall comply with SEMI E30 rules to ensure safe and controlled equipment operation.

    - The system shall validate all remote commands received from the Host prior to execution.

    - Remote command validation shall include:

- Command name validity.

- Required parameter presence and format.

- Current communication state and control state checks

    - Only authorized and valid remote commands shall be executed on the equipment.

    - Valid remote commands shall be executed through the Equipment Adapter interface.

    - The system shall detect errors during remote command processing or execution.

    - Remote command error conditions shall include:

- Invalid or unsupported commands

- Missing or incorrect command parameters

- Control or communication state violations.

- Equipment-level execution failures

    - The system shall report remote command errors to the Host using standard GEM response codes.

    - All remote command attempts and errors shall be logged for diagnostics, troubleshooting, and traceability.

## Recipe Management

    - The system shall support GEM recipe management in accordance with SEMI E30.

    - The system shall allow the Host to list available recipes on the equipment.

    - The system shall support recipe upload from the Host to the equipment.

    - The system shall support recipe download from the equipment to the Host.

    - Recipe transfer operations shall comply with SECS-II Stream 7 requirements.

    - The system shall support recipe validation to ensure correctness and completeness prior to use.

    - Only validated recipes shall be eligible for activation on the equipment.

    - The system shall allow the Host to select and activate recipes in accordance with GEM rules.

    - Recipe activation shall be subject to equipment state, control state, and safety conditions.

    - Recipe validation and activation shall comply with SEMI E30 requirements.

    - The system shall provide persistent storage for equipment recipes.

    - The system shall support multiple recipes and retain them across system restarts.

    - Recipe modifications shall be tracked using version information or unique identifiers.

    - The system shall ensure recipe integrity during storage, transfer, and activation.

    - Recipe storage and version control shall support reliable and repeatable equipment operation.

## Terminal Services

    - The system shall support GEM terminal services using SECS-II Stream 10 (S10).

    - The system shall receive and process terminal messages sent by the Host.

    - Terminal messages shall be managed as informational or diagnostic communication only.

    - The system shall acknowledge terminal messages in accordance with SEMI E30 requirements.

    - Terminal message handling shall not interfere with normal equipment operation.

    - The system shall provide a means to display terminal messages to the operator when required.

    - Displayed terminal messages shall include:

- Message content

- Timestamp

    - Operator interaction with terminal messages shall be informational only.

    - Terminal message display shall not allow direct control of equipment operations.

    - Operator interaction with terminal services shall comply with GEM rules and equipment safety guidelines.

    - The system shall log all terminal messages exchanged with the Host.

    - Logged terminal message information shall include:

- Message content

- Timestamp

- Message direction (Host → Equipment or Equipment → Host)

    - Terminal message logs shall be retained for diagnostics, troubleshooting, and audit purposes.

    - Logging of terminal messages shall not impact normal GEM communication performance.

## Time Management

    - The system shall manage protocol-related timers in accordance with SEMI E37 and SEMI E30.

    - The system shall support required timers for HSMS and SECS-II communication.

    - Protocol timer values shall be configurable, with default values aligned to SEMI recommendations.

    - Expiration of protocol timers shall trigger appropriate error handling and recovery actions.

    - Protocol timer management shall ensure stable and dependable Host–Equipment communication.

    - The system shall maintain correct sequencing of all GEM messages exchanged with the Host.

    - Messages shall be processed and reported in the order of occurrence.

    - The system shall assign timestamps to the following GEM activities:

- Alarms

- Events

- Reports

- Remote commands

    - Timestamps shall use a consistent and unified system time reference.

    - Message sequencing and timestamping shall support traceability and audit requirements.

    - The system shall maintain a consistent internal time reference for all GEM operations.

    - The system shall support synchronization with the equipment system clock.

    - Time synchronization shall ensure accurate timestamps for alarms, events, and reports.

    - Time handling shall remain stable across system restarts and reconnections.

    - Time synchronization shall support reliable data correlation with factory Host systems.

# System Architecture Requirements

## Logical Architecture Overview

    - The GEM-200 system shall be designed using a modular and layered architecture.

    - The architecture shall clearly separate the following functional concerns:

- Communication handling

- SECS-II protocol processing

- GEM business logic

- Equipment-specific integration

    - The GEM Controller shall be independent of equipment hardware using a defined Equipment Adapter interface.

    - Each architectural component shall be loosely coupled to minimize dependencies between modules.

    - Each architectural component shall be independently testable.

    - The architecture shall support scalability, maintainability, and reuse across different 200 mm semiconductor equipment platforms.

## GEM-200 Core Components

The GEM-200 system is implemented as a modular, layered architecture composed of well-defined core components. The design ensures compliant Host–Equipment communication, clear separation of responsibilities, and easy integration with different equipment platforms.

    - HSMS Communication Layer

The HSMS Communication Layer shall manage all TCP/IP communication between the equipment and the Host in accordance with SEMI E37. The layer shall support HSMS-SS session establishment, maintenance, and termination, and shall manage HSMS control messages and session state transitions. It shall manage protocol timers, detect communication errors, and deliver only validated HSMS messages to the upper GEM processing layers.

    - SECS Message Parser / Builder

The SECS Message Parser / Builder shall process SECS-II messages in accordance with SEMI E5. The component shall decode incoming messages, construct compliant reply to messages, and manage SECS-II header fields and overall message structure. It shall validate message formats and data types, and only valid SECS-II messages shall be forwarded to GEM processing components.

    - Message Dispatcher

The Message Dispatcher shall route incoming SECS-II messages to the appropriate GEM function or handler based on the message stream and function (SxFy). The dispatcher shall ensure that mandatory replies are generated for messages requiring a response and shall support asynchronous message processing to maintain system responsiveness. All message transactions shall be logged for traceability.

    - Event & Report Engine

The Event & Report Engine shall manage GEM event and report processing in accordance with SEMI E30. The engine shall maintain CEID, RPTID, and VID associations and shall generate event reports (S6F11) when configured events occur. It shall collect and include current VID values in event reports, ensuring that event and report handling follows GEM timing and formatting rules.

    - Alarm Engine

The Alarm Engine shall manage GEM alarm processing in accordance with SEMI E30. The engine shall maintain alarm definitions and alarm states and shall generate alarm reports when alarms are set or cleared. It shall support Host queries for both defined and active alarms and shall integrate with the Event & Report Engine to trigger CEID generation.

    - Variable Data Model

The Variable Data Model shall manage VID and SVID definitions in accordance with SEMI E30. The model shall provide current variable values required for GEM reporting and Host queries, retrieving values from the equipment through the Equipment Adapter interface. It shall support the use of variables in events, reports, trace data, and remote commands while ensuring accuracy, consistency, and reliability.

    - Remote Command Engine

The Remote Command Engine shall process GEM remote commands in accordance with SEMI E30. The engine shall validate command names, parameters, and execution conditions and shall enforce communication and control state requirements before execution. Valid commands shall be executed through the Equipment Adapter interface, and command execution results shall be reported back to the Host.

    - Recipe Manager

The Recipe Manager shall manage GEM recipe operations in accordance with SEMI E30. The component shall support recipe listing, upload, download, validation, and activation. Recipes shall be stored and retrieved using persistent storage mechanisms, and the Recipe Manager shall interface with the Equipment Adapter for equipment-specific recipe handling, ensuring integrity, consistency, and repeatability of equipment operation.

    - Control & Communication State Machines

The system shall implement GEM-compliant communication and control state machines in accordance with SEMI E30. The Communication State Machine shall manage OFFLINE, ATTEMPT ONLINE, ONLINE LOCAL, and ONLINE REMOTE states, while the Control State Machine shall manage LOCAL and REMOTE states. The state machines shall enforce valid state transitions based on Host commands and equipment conditions, control system behaviour such as command permissions and reporting, and report state transitions to the Host as required by GEM.

    - Equipment Adapter Interface

The Equipment Adapter Interface shall provide a standardized integration layer between the GEM Controller and equipment control systems. The interface shall isolate equipment-specific logic from core GEM functionality and shall provide access to equipment status, process state, variable data (VID/SVID values), alarm information, event notifications, and recipe load and save operations. The interface shall execute equipment control commands issued by the GEM Controller and shall enable reuse of the GEM Controller across different 200 mm equipment platforms.

# Equipment Adapter Requirements

## Equipment Control Interface

    - The Equipment Control Interface shall provide standard methods to execute equipment control actions.

    - The interface shall support start, stop, reset, and other supported control commands.

    - Control commands shall be executed only when permitted by GEM communication and control states.

    - The interface shall enforce equipment safety and interlock conditions before execution.

    - Control interface behaviour shall ensure safe and predictable equipment operation.

## Equipment Status Interface

    - The Equipment Status Interface shall provide current equipment operational status to the GEM Controller.

    - The interface shall report equipment state, mode, and readiness information.

    - Status information shall be used for GEM state management, reporting, and Host queries.

    - Status updates shall reflect real-time equipment conditions.

    - The interface shall ensure accurate and consistent status reporting to the Host.

## Equipment Alarm Interface

    - The Equipment Alarm Interface shall provide equipment-level alarm information to the GEM Controller.

    - The interface shall map equipment alarms to corresponding GEM alarm identifiers (ALIDs).

    - Alarm set and clear conditions shall be reported accurately and in real time.

    - Alarm information shall be used for GEM alarm reporting and Host queries.

    - The interface shall ensure consistency between equipment alarms and GEM alarm status.

## Equipment Event Interface

    - The Equipment Event Interface shall provide equipment-generated events to the GEM Controller.

    - The interface shall notify the GEM Controller of process, state, and operational events.

    - Equipment events shall be mapped to corresponding GEM Collection Event IDs (CEIDs).

    - Event notifications shall be used to trigger GEM event reporting to the Host.

    - The interface shall ensure timely and accurate event propagation without impacting equipment operation.

  - Equipment Recipe Interface

    - The Equipment Recipe Interface shall provide equipment-level support for recipe operations.

    - The interface shall support loading, saving, and activating recipes on the equipment.

    - Recipe data shall be exchanged between the GEM Controller and equipment in a controlled and consistent manner.

    - The interface shall ensure recipe integrity and correctness during transfer and execution.

    - Equipment recipe operations shall align with GEM recipe management requirements.

# Configuration Management

## Configuration Storage

    - The system shall provide persistent storage for all GEM-200 configuration data.

    - Configuration storage shall include:

        - HSMS communication settings

        - Alarm, event, report, and variable definitions.

        - Remote command definitions

        - Recipe-related configuration

        - Simulation and optional feature settings

    - Configuration data shall be externally configurable without source code changes.

    - Stored configuration shall be retained across system restarts.

    - Configuration storage shall support reliable and consistent GEM operation.

## Runtime Configuration Handling

    - The system shall support runtime loading and application of configuration settings.

    - Configuration changes shall be applied without requiring a system restart, where feasible.

    - Runtime configuration updates shall be validated before being applied.

    - Invalid configuration changes shall be rejected and logged.

    - Runtime handling shall not disrupt active GEM communication or equipment operation.

## Version and Change Control

    - The system shall maintain version information for configuration data.

    - Configuration changes shall be tracked and auditable.

    - The system shall support rollback or recovery to a previous configuration when required.

    - Version and change control shall ensure configuration consistency and traceability.

    - Configuration management shall support reliable long-term operation and client audits.

# Logging and Diagnostics

## HSMS and SECS-II Message Logging

    - The system shall log HSMS and SECS-II message traffic exchanged with the Host.

    - Logged information shall include:

- Message direction (Host ↔ Equipment)

- Stream and Function (SxFy)

- Timestamp

    - Logging shall support diagnostics, troubleshooting, and audit requirements.

    - Message logging shall not impact normal GEM communication performance.

## Alarm and Event History

    - The system shall maintain a history of alarm and event activities.

    - Alarm history shall include:

- Alarm set and clear events

- Alarm identifiers and timestamps.

    - Event history shall include:

- Triggered CEIDs

- Associated timestamps

    - Historical data shall be available for diagnostics, analysis, and client audits.

    - Alarm and event history handling shall ensure data accuracy and consistency.

## Remote Command and Adapter Logging

    - The system shall log all remote command requests and execution results.

    - Logged information shall include:

- Command name and parameters.

- Execution status (success or failure)

- Timestamp

    - The system shall log interactions with the Equipment Adapter, including:

- Command dispatch

- Data access requests

- Error conditions

    - Logs shall support diagnostics, troubleshooting, and compliance audits.

    - Logging shall not impact normal equipment or GEM operation.

## Log Retention and Rotation

    - The system shall support log retention policies configurable by time or size.

    - The system shall perform automatic log rotation to prevent uncontrolled log growth.

    - Archived logs shall be protected from overwrite or loss.

    - Log retention settings shall support factory audit and compliance requirements.

    - Log rotation and retention shall operate without impacting system performance.

# Reliability and Data Integrity

## Spooling Requirements

    - The system shall support message spooling to prevent data loss during temporary Host communication interruptions.

    - Events, alarms, and reports generated while disconnected shall be queued securely.

    - Spooled messages shall be transmitted automatically when communication is restored.

    - Message delivery shall preserve the original order of occurrence.

    - Spooling capacity and behaviour shall be configurable.

    - Spooling shall ensure data integrity and GEM compliance without impacting normal operation.

## Message Recovery and Reconnect Handling

    - The system shall detect Host disconnections and communication failures.

    - Upon reconnection, the system shall recover the HSMS session in accordance with SEMI E37.

    - Spooled messages shall be resumed and delivered automatically after reconnection.

    - Message recovery shall maintain correct sequencing and completeness.

    - Reconnect handling shall ensure no data loss and no duplicate reporting.

    - Recovery behaviour shall not disrupt ongoing equipment operation.

## Data Consistency Guarantees

    - The system shall ensure consistent and accurate data reporting to the Host.

    - Reported alarms, events, variables, and command results shall reflect the actual equipment state.

    - Data consistency shall be maintained across:

- Communication interruptions

- System restarts

- Configuration changes

    - The system shall prevent duplicate, missing, or out-of-order data reporting.

    - Data integrity mechanisms shall support reliable factory operation and audits.

# Optional Engineering Features

## Simulation Mode

    - The system may support a Simulation Mode for engineering and testing purposes.

    - Simulation Mode shall allow GEM functionality to operate without physical equipment.

    - The system may simulate:

- Communication and control state transitions

- Alarms, events, and reports

- Variable data (VID / SVID values)

- Remote command responses

- Recipe lists and content

    - Simulation Mode shall be configurable and disabled in production environments.

    - Simulation Mode shall not affect mandatory GEM-200 compliance behaviour.

## Host Simulator

    - The system may provide a Host Simulator for engineering, testing, and validation purposes.

    - The Host Simulator may simulate factory Host behaviour for GEM communication.

    - The simulator may support:

- HSMS session establishment and control messages

- SECS-II message exchange

- Event, alarm, and command interactions

    - The Host Simulator shall be used only for non-production environments.

    - Use of the Host Simulator shall not impact production GEM-200 operation.

## Equipment Simulator

    - The system may provide an Equipment Simulator for engineering and testing purposes.

    - The Equipment Simulator may simulate equipment behaviour without physical hardware.

    - The simulator may support:

- Communication and control state changes

- Alarm and event generation.

- Variable data (VID / SVID) updates

- Remote command execution behaviour

- Recipe handling scenarios

    - The Equipment Simulator shall support Host integration testing and demonstrations.

    - The simulator shall be used only in non-production environments and shall not affect GEM-200 compliance.

## Diagnostic / Engineering User Interface

    - The system may provide a Diagnostic / Engineering User Interface (UI) for support and testing purposes.

    - The UI may display:

- HSMS connection status

- Communication and control states

- Active alarms and event history

- GEM message and diagnostic information

    - The UI may allow controlled testing actions (e.g., simulation toggles, command tests) in non-production environments.

    - The UI shall be restricted to authorized users.

    - The Diagnostic / Engineering UI shall not interfere with normal equipment operation or GEM-200 compliance.

# Performance Requirements

  - The system shall support continuous operation in automated 200 mm factory environments.

  - The system shall process HSMS and SECS-II messages within timing limits defined by SEMI standards.

  - Event, alarm, and report generation shall occur without undue latency.

  - The system shall manage normal and peak message loads without degradation of GEM functionality.

  - Performance behaviour shall not impact equipment safety or production stability.

# Security Requirements

  - The system shall support secure operation in accordance with factory IT and OEM security policies.

  - Access to configuration, diagnostic tools, and optional user interfaces shall be restricted to authorized users.

  - The system shall protect configuration data, logs, and operational data from unauthorized modification.

  - Security controls shall not interfere with mandatory GEM-200 communication and compliance behaviour.

  - Any optional security mechanisms shall be configurable and suitable for non-production and production environments.

# Verification and Test Requirements

## SEMI GEM Mandatory Test Coverage

    - The system shall support verification against mandatory SEMI GEM test cases.

    - Testing shall confirm compliance with:

        - SEMI E30 (GEM)

        - SEMI E37 (HSMS-SS)

        - SEMI E5 (SECS-II)

    - Mandatory test coverage shall include:

    - HSMS communication and session handling

    - SECS-II message processing

    - GEM state models

    - Alarm, event, and report handling.

    - Variable data reporting

    - Remote command execution

    - Recipe management

    - Test results shall be documented and available for client review and factory acceptance.

## Host Integration Testing

    - The system shall support integration testing with a factory Host system.

    - Host integration testing shall verify:

          - HSMS session establishment and recovery

          - SECS-II message exchange

          - GEM state transitions

          - Alarm, event, and report communication.

          - Variable data queries and updates

          - Remote command execution

    - Integration testing shall confirm interoperability and stable operation with the Host.

    - Test outcomes shall be recorded and reviewed as part of client acceptance.

## Factory Acceptance Testing (FAT)

    - The system shall support Factory Acceptance Testing (FAT) prior to delivery or deployment.

    - FAT shall validate:

        - GEM-200 functional requirements

        - SEMI standard compliance

        - Host–Equipment communication stability.

    - FAT shall be conducted using defined test procedures and acceptance criteria.

    - Any deviations identified during FAT shall be documented and resolved.

    - Successful FAT completion shall be required for final client acceptance and sign-off.

# Supported SECS-II Streams and Functions

  - Stream 1 – Equipment Status Messages

| Request | Response | Description |
| --- | --- | --- |
| S1F1 | S1F2 | Are You Their request to verify equipment communication |
| S1F3 | S1F4 | Selected equipment status request |
| S1F11 | S1F12 | Status variable name list request |
| S1F13 | S1F14 | Establish communication request |
| S1F15 | S1F16 | Request equipment to go OFF-LINE |
| S1F17 | S1F18 | Request equipment to go ON-LINE |

  - Stream 2 – Equipment Control and Data Collection

| Request | Response | Description |
| --- | --- | --- |
| S2F13 | S2F14 | Equipment constants send |
| S2F15 | S2F16 | New equipment constant sends |
| S2F17 | S2F18 | Date and time request |
| S2F23 | S2F24 | Trace initializes send |
| S2F25 | S2F26 | Loopback diagnostic request |
| S2F29 | S2F30 | Equipment constant name list request |
| S2F31 | S2F32 | Date and time set request |
| S2F33 | S2F34 | Define report |
| S2F35 | S2F36 | Link event report (LER) |
| S2F37 | S2F38 | Enable / disable event report |
| S2F39 | S2F40 | Multiblock inquire |
| S2F41 | S2F42 | Host remote command |
| S2F43 | S2F44 | Reset spooling streams and functions (RSSF) |
| S2F45 | S2F46 | Define variable limit attributes (DVLA) |
| S2F47 | S2F48 | Variable limit attribute request (VLAR) |
| S2F49 | S2F50 | Enhanced remote command |

  - Stream 3 – Carrier and Port Handling

| Request | Response | Description |
| --- | --- | --- |
| S3F17 | S3F18 | Carrier action request |
| S3F25 | S3F26 | Port action request |
| S3F27 | S3F28 | Load port access mode change request |

  - Stream 5 – Alarm Management

| Request | Response | Description |
| --- | --- | --- |
| S5F3 | S5F4 | Enable / disable alarm sends |
| S5F5 | S5F6 | List alarms request |
| S5F7 | S5F8 | List enabled alarm request |

  - Stream 6 – Event and Trace Reporting

| Request | Response | Description |
| --- | --- | --- |
| S6F1 | S6F2 | Trace data send |
| S6F5 | S6F6 | Multi-block data send inquire |
| S6F11 | S6F12 | Event report send |
| S6F19 | S6F20 | Individual report request |
| S6F23 | S6F24 | Request spooled data |

  - Stream 7 – Recipe Management

| Request | Response | Description |
| --- | --- | --- |
| S7F1 | S7F2 | Process program load inquires |
| S7F3 | S7F4 | Process programs send |
| S7F5 | S7F6 | Process program request |
| S7F17 | S7F18 | Delete process program send |
| S7F19 | S7F20 | Current EPPD request |

  - Stream 9 – Error Messages

| Request | Response | Description |
| --- | --- | --- |
| S9F1 | S9F2 | Unrecognized Device ID |
| S9F3 | S9F4 | Unrecognized stream type |
| S9F5 | S9F6 | Unrecognized function type |
| S9F7 | S9F8 | Illegal data |
| S9F9 | S9F10 | Transaction timer timeout |
| S9F11 | S9F12 | Data too long |

  - Stream 10 – Terminal Services

| Request | Response | Description |
| --- | --- | --- |
| S10F1 | S10F2 | Terminal request |
| S10F3 | S10F4 | Terminal display – single |
| S10F5 | S10F6 | Terminal display – multi-block |